## README
PV MASTER RESULTS — CURRENT PEREZ–DRIESSE ANALYSIS | Value / description
Generated | 2026-09-28 13:07:53
Status | CURRENT Perez–Driesse master results candidate
Purpose | Single source of article result values assembled from 02_run_analysis.py outputs. This workbook does NOT recompute metrics.
Annual canonical dataset | 26208 rows; 8736 unique timestamps; systems A, B, C
Measured GTI | A = GTI3M with verified +1 h correction; B/C = GTI9M.
Annual record rules | GTI/Tp: measured GTI > 0 and paired non-missing values; Power: same daytime rule plus exactly four agreed gross-error timestamps; no additional outlier removal.
Monthly RMSE/kWp | Uses the same daytime-cleaned power records; nighttime PVsyst inverter consumption is intentionally excluded.
Weather bins | kt_tilt = measured GTI / Eext_tilt; full azimuth-aware AOI; AOI < 80°; bins <0.2, 0.2–0.4, 0.4–0.6, 0.6–0.75, >=0.75; no upper kt_tilt cap.
Geometry | 57.719231 N, 12.884806 E, 170 m; tilt 45°; pvlib azimuth 180°; Eext_normal uses documented Esc=1361.1 W/m² formulation.
Logger clock | Raw RISE timestamps empirically identified as Europe/Stockholm civil time (CET/CEST).
Shading | Definitive audited reconstruction; no additional outlier removal.
Old frozen workbook | Superseded as authority because it may contain mixed Engerer2 / Perez–Driesse generations. Retain only as historical audit material.
QA: Annual GTI rows | PASS — expected 6, actual 6
QA: Annual temperature rows | PASS — expected 6, actual 6
QA: Annual power rows | PASS — expected 6, actual 6
QA: Monthly RMSE rows | PASS — expected 6, actual 6
QA: Weather-bin rows | PASS — expected 30, actual 30
QA: Shading energy rows | PASS — expected 18, actual 18
QA: Shading hourly diagnostic rows | PASS — expected 6, actual 6

## Annual_GTI
System | Software | n | mean_measured | RMSE | MAE | CVRMSE_percent | nMAE_percent | MBE | nMBE_percent | RE_percent | R2
A | IDA ICE | 4635 | 232.8119 | 15.3363 | 10.1623 | 6.5874 | 4.365 | -9.334 | -4.0092 | -4.0092 | 0.99674
A | PVsyst | 4635 | 232.8119 | 22.4383 | 15.8832 | 9.638 | 6.8223 | -15.75 | -6.7651 | -6.7651 | 0.99302
B | IDA ICE | 5351 | 197.4834 | 21.7376 | 10.0664 | 11.0073 | 5.0973 | -7.4245 | -3.7595 | -3.7595 | 0.99317
B | PVsyst | 5351 | 197.4834 | 25.0612 | 13.8645 | 12.6903 | 7.0206 | -12.3311 | -6.2441 | -6.2441 | 0.99093
C | IDA ICE | 5351 | 197.4834 | 21.6221 | 9.9493 | 10.9488 | 5.038 | -7.2229 | -3.6575 | -3.6575 | 0.99325
C | PVsyst | 5351 | 197.4834 | 26.8748 | 15.6754 | 13.6086 | 7.9376 | -14.1774 | -7.179 | -7.179 | 0.98957

## Annual_Temperature
System | Software | n | mean_measured | RMSE | MAE | CVRMSE_percent | nMAE_percent | MBE | nMBE_percent | RE_percent | R2
A | IDA ICE | 4635 | 15.3679 | 5.1013 | 3.566 | 33.1947 | 23.204 | 2.5802 | 16.7897 | 16.7897 | 0.83562
A | PVsyst | 4635 | 15.3679 | 5.6627 | 4.1475 | 36.8475 | 26.9879 | 2.2986 | 14.9571 | 14.9571 | 0.79745
B | IDA ICE | 5351 | 14.4711 | 4.7172 | 3.3059 | 32.5974 | 22.845 | 1.1289 | 7.8011 | 7.8011 | 0.84745
B | PVsyst | 5351 | 14.4711 | 6.3993 | 4.4376 | 44.2209 | 30.6651 | 0.72761 | 5.028 | 5.028 | 0.71926
C | IDA ICE | 4828 | 17.5758 | 4.44 | 3.0585 | 25.2623 | 17.4017 | -1.4256 | -8.1112 | -8.1112 | 0.93184
C | PVsyst | 4828 | 17.5758 | 5.5856 | 3.8606 | 31.7803 | 21.9655 | -0.3151 | -1.7928 | -1.7928 | 0.89214

## Annual_Power
System | Software | Common_power_timestamps_removed | RMSE_month_kWh_per_kWp | n | mean_measured | RMSE | MAE | CVRMSE_percent | nMAE_percent | MBE | nMBE_percent | RE_percent | R2
A | IDA ICE | 4 | 2.9178 | 4631 | 761.2563 | 262.1458 | 167.3538 | 34.4359 | 21.9839 | 14.0566 | 1.8465 | 1.8465 | 0.91754
A | PVsyst | 4 | 4.1685 | 4631 | 761.2563 | 257.2306 | 164.9329 | 33.7903 | 21.6659 | -24.7124 | -3.2463 | -3.2463 | 0.9206
B | IDA ICE | 4 | 5.7028 | 5347 | 770.04 | 320.5248 | 179.227 | 41.6244 | 23.275 | 48.0584 | 6.241 | 6.241 | 0.91108
B | PVsyst | 4 | 2.7157 | 5347 | 770.04 | 294.335 | 161.7188 | 38.2233 | 21.0014 | 16.7882 | 2.1802 | 2.1802 | 0.92502
C | IDA ICE | 4 | 9.199 | 5347 | 509.6367 | 245.0861 | 135.3857 | 48.0903 | 26.5651 | 50.3466 | 9.8789 | 9.8789 | 0.89105
C | PVsyst | 4 | 11.3616 | 5347 | 509.6367 | 230.4953 | 127.0654 | 45.2274 | 24.9325 | 68.2501 | 13.3919 | 13.3919 | 0.90363

## Monthly_RMSE
System | Software | kWp | n_months | RMSE_month_kWh | RMSE_month_kWh_per_kWp
A | IDA ICE | 3.9 | 12 | 11.3795 | 2.9178
A | PVsyst | 3.9 | 12 | 16.257 | 4.1685
B | IDA ICE | 4.8 | 12 | 27.3733 | 5.7028
B | PVsyst | 4.8 | 12 | 13.0354 | 2.7157
C | IDA ICE | 3.3 | 12 | 30.3568 | 9.199
C | PVsyst | 3.3 | 12 | 37.4932 | 11.3616

## Weather_Bins
System | Sky_condition | kt_min | kt_max | Software | n | mean_measured | RMSE | MAE | CVRMSE_percent | nMAE_percent | MBE | nMBE_percent | RE_percent | R2
A | Overcast/very cloudy | 0 | 0.2 | IDA ICE | 1713 | 211.8795 | 142.6249 | 78.7722 | 67.3142 | 37.1778 | -8.7137 | -4.1126 | -4.1126 | 0.70121
A | Overcast/very cloudy | 0 | 0.2 | PVsyst | 1713 | 211.8795 | 137.6264 | 72.8604 | 64.955 | 34.3877 | -12.8829 | -6.0803 | -6.0803 | 0.72178
A | Cloudy | 0.2 | 0.4 | IDA ICE | 651 | 845.318 | 325.8532 | 255.6013 | 38.548 | 30.2373 | 107.4854 | 12.7154 | 12.7154 | 0.5046
A | Cloudy | 0.2 | 0.4 | PVsyst | 651 | 845.318 | 310.0629 | 239.7571 | 36.68 | 28.363 | 63.2554 | 7.483 | 7.483 | 0.55145
A | Mixed/broken | 0.4 | 0.6 | IDA ICE | 497 | 1617.1499 | 445.137 | 367.9939 | 27.526 | 22.7557 | 189.3153 | 11.7067 | 11.7067 | 0.4002
A | Mixed/broken | 0.4 | 0.6 | PVsyst | 497 | 1617.1499 | 409.4331 | 332.8335 | 25.3182 | 20.5815 | 101.7948 | 6.2947 | 6.2947 | 0.49256
A | Mostly clear | 0.6 | 0.75 | IDA ICE | 336 | 2475.9879 | 394.2061 | 297.3623 | 15.9212 | 12.0098 | 122.515 | 4.9481 | 4.9481 | 0.61717
A | Mostly clear | 0.6 | 0.75 | PVsyst | 336 | 2475.9879 | 375.1295 | 296.9788 | 15.1507 | 11.9944 | -37.2814 | -1.5057 | -1.5057 | 0.65333
A | Clear | 0.75 |  | IDA ICE | 337 | 2303.1401 | 350.7667 | 287.9792 | 15.2299 | 12.5038 | -109.1914 | -4.741 | -4.741 | 0.74072
A | Clear | 0.75 |  | PVsyst | 337 | 2303.1401 | 401.0179 | 359.8103 | 17.4118 | 15.6226 | -251.1395 | -10.9042 | -10.9042 | 0.66111
B | Overcast/very cloudy | 0 | 0.2 | IDA ICE | 1827 | 242.4531 | 181.0286 | 100.8154 | 74.6654 | 41.5814 | -2.9692 | -1.2247 | -1.2247 | 0.65645
B | Overcast/very cloudy | 0 | 0.2 | PVsyst | 1827 | 242.4531 | 172.8227 | 92.8363 | 71.2809 | 38.2904 | 3.7651 | 1.5529 | 1.5529 | 0.68689
B | Cloudy | 0.2 | 0.4 | IDA ICE | 611 | 1032.2701 | 454.3769 | 369.4714 | 44.0172 | 35.7921 | 186.9837 | 18.1138 | 18.1138 | 0.41748
B | Cloudy | 0.2 | 0.4 | PVsyst | 611 | 1032.2701 | 419.2508 | 329.8869 | 40.6144 | 31.9574 | 114.9225 | 11.133 | 11.133 | 0.50407
B | Mixed/broken | 0.4 | 0.6 | IDA ICE | 469 | 1966.3175 | 581.498 | 470.0925 | 29.5729 | 23.9073 | 284.8902 | 14.4885 | 14.4885 | 0.36732
B | Mixed/broken | 0.4 | 0.6 | PVsyst | 469 | 1966.3175 | 525.7504 | 406.4038 | 26.7378 | 20.6683 | 156.372 | 7.9525 | 7.9525 | 0.48282
B | Mostly clear | 0.6 | 0.75 | IDA ICE | 311 | 3005.0825 | 484.0586 | 364.7746 | 16.108 | 12.1386 | 225.5907 | 7.507 | 7.507 | 0.58947
B | Mostly clear | 0.6 | 0.75 | PVsyst | 311 | 3005.0825 | 429.9252 | 322.5754 | 14.3066 | 10.7343 | 42.3278 | 1.4085 | 1.4085 | 0.67616
B | Clear | 0.75 |  | IDA ICE | 350 | 2764.4097 | 557.4638 | 345.2145 | 20.1657 | 12.4878 | 74.3031 | 2.6878 | 2.6878 | 0.63295
B | Clear | 0.75 |  | PVsyst | 350 | 2764.4097 | 528.6875 | 369.7816 | 19.1248 | 13.3765 | -54.9623 | -1.9882 | -1.9882 | 0.66987
C | Overcast/very cloudy | 0 | 0.2 | IDA ICE | 1827 | 138.9228 | 125.5317 | 64.7519 | 90.3608 | 46.61 | -12.3418 | -8.884 | -8.884 | 0.65516
C | Overcast/very cloudy | 0 | 0.2 | PVsyst | 1827 | 138.9228 | 130.3364 | 75.8537 | 93.8193 | 54.6013 | 30.9433 | 22.2737 | 22.2737 | 0.62826
C | Cloudy | 0.2 | 0.4 | IDA ICE | 611 | 686.6083 | 326.5785 | 265.4537 | 47.564 | 38.6616 | 123.8443 | 18.0371 | 18.0371 | 0.43328
C | Cloudy | 0.2 | 0.4 | PVsyst | 611 | 686.6083 | 343.8738 | 283.563 | 50.083 | 41.2991 | 173.1524 | 25.2185 | 25.2185 | 0.37166
C | Mixed/broken | 0.4 | 0.6 | IDA ICE | 469 | 1344.4597 | 436.653 | 362.7521 | 32.478 | 26.9813 | 240.4918 | 17.8876 | 17.8876 | 0.29632
C | Mixed/broken | 0.4 | 0.6 | PVsyst | 469 | 1344.4597 | 431.1267 | 356.685 | 32.0669 | 26.53 | 245.2585 | 18.2422 | 18.2422 | 0.31402
C | Mostly clear | 0.6 | 0.75 | IDA ICE | 311 | 2052.9757 | 449.5008 | 382.4513 | 21.8951 | 18.6291 | 311.5398 | 15.175 | 15.175 | 0.23259
C | Mostly clear | 0.6 | 0.75 | PVsyst | 311 | 2052.9757 | 364.0345 | 285.8458 | 17.732 | 13.9235 | 212.4638 | 10.3491 | 10.3491 | 0.49667
C | Clear | 0.75 |  | IDA ICE | 350 | 1886.4931 | 430.1902 | 284.4191 | 22.8037 | 15.0766 | 166.6386 | 8.8332 | 8.8332 | 0.5147
C | Clear | 0.75 |  | PVsyst | 350 | 1886.4931 | 369.5228 | 203.5315 | 19.5878 | 10.7889 | 124.7169 | 6.611 | 6.611 | 0.64192

## Shading_Energy
period | System | Software | n_intervals | measured_kWh | simulated_kWh | difference_kWh | difference_fraction | difference_percent
Clear_day_2023-06-05 | A | IDA ICE | 24 | 24.211 | 23.5509 | -0.66007 | -0.027263 | -2.7263
Clear_day_2023-06-05 | A | PVsyst | 24 | 24.211 | 24.8915 | 0.6805 | 0.028107 | 2.8107
Clear_day_2023-06-05 | B | IDA ICE | 24 | 30.915 | 28.5841 | -2.3309 | -0.075396 | -7.5396
Clear_day_2023-06-05 | B | PVsyst | 24 | 30.915 | 30.1111 | -0.8039 | -0.026004 | -2.6004
Clear_day_2023-06-05 | C | IDA ICE | 24 | 20.188 | 21.2487 | 1.0607 | 0.052542 | 5.2542
Clear_day_2023-06-05 | C | PVsyst | 24 | 20.188 | 21.7475 | 1.5595 | 0.077249 | 7.7249
Partly_cloudy_day_2023-05-15 | A | IDA ICE | 24 | 11.281 | 11.3287 | 0.047667 | 0.0042254 | 0.42254
Partly_cloudy_day_2023-05-15 | A | PVsyst | 24 | 11.281 | 11.7826 | 0.5016 | 0.044464 | 4.4464
Partly_cloudy_day_2023-05-15 | B | IDA ICE | 24 | 13.867 | 12.6768 | -1.1902 | -0.085827 | -8.5827
Partly_cloudy_day_2023-05-15 | B | PVsyst | 24 | 13.867 | 14.0736 | 0.2066 | 0.014899 | 1.4899
Partly_cloudy_day_2023-05-15 | C | IDA ICE | 24 | 8.856 | 9.215 | 0.35903 | 0.040541 | 4.0541
Partly_cloudy_day_2023-05-15 | C | PVsyst | 24 | 8.856 | 9.7397 | 0.8837 | 0.099785 | 9.9785
Full_period_2023-05-01_to_2023-06-19 | A | IDA ICE | 1200 | 1021.408 | 1019.3436 | -2.0644 | -0.0020211 | -0.20211
Full_period_2023-05-01_to_2023-06-19 | A | PVsyst | 1200 | 1021.408 | 1020.6063 | -0.8017 | -0.0007849 | -0.07849
Full_period_2023-05-01_to_2023-06-19 | B | IDA ICE | 1200 | 1319.352 | 1220.7186 | -98.6334 | -0.074759 | -7.4759
Full_period_2023-05-01_to_2023-06-19 | B | PVsyst | 1200 | 1319.352 | 1294.1203 | -25.2317 | -0.019124 | -1.9124
Full_period_2023-05-01_to_2023-06-19 | C | IDA ICE | 1200 | 867.19 | 901.4112 | 34.2212 | 0.039462 | 3.9462
Full_period_2023-05-01_to_2023-06-19 | C | PVsyst | 1200 | 867.19 | 936.6602 | 69.4702 | 0.08011 | 8.011

## Shading_Hourly
System | Software | n | mean_measured | RMSE | MAE | CVRMSE_percent | nMAE_percent | MBE | nMBE_percent | RE_percent | R2
A | IDA ICE | 932 | 1095.8809 | 278.1762 | 179.0142 | 25.3838 | 16.3352 | -2.1646 | -0.19752 | -0.19752 | 0.93717
A | PVsyst | 932 | 1095.8809 | 251.7784 | 158.8906 | 22.975 | 14.4989 | -0.84914 | -0.077485 | -0.077485 | 0.94852
B | IDA ICE | 886 | 1488.9842 | 566.9802 | 421.6253 | 38.0783 | 28.3163 | -111.198 | -7.468 | -7.468 | 0.8437
B | PVsyst | 886 | 1488.9842 | 198.833 | 114.5949 | 13.3536 | 7.6962 | -28.3699 | -1.9053 | -1.9053 | 0.98078
C | IDA ICE | 886 | 978.7698 | 182.6585 | 104.623 | 18.6621 | 10.6892 | 38.6244 | 3.9462 | 3.9462 | 0.96518
C | PVsyst | 886 | 978.7698 | 253.6952 | 140.0418 | 25.9198 | 14.3079 | 78.4088 | 8.011 | 8.011 | 0.93283

## Power_Exclusions
System | daytime_rows_before_power_exclusions | power_rows_after_four_timestamp_exclusions | rows_removed
A | 4635 | 4631 | 4
B | 5351 | 5347 | 4
C | 5351 | 5347 | 4

## Provenance
component | source | status | note
Measured raw source | RISE_raw10min_389.xlsx | AUDITED | Raw source retained. Historical processed power not fully reconstructible from available raw Power_*.
Measured canonical layer | Results_PVsyst_E2_hour.xlsx measured columns only | AUTHORITATIVE_PROCESSED_LAYER | All historical E2 simulation columns explicitly excluded.
IDA ICE A/B/C | Syst3_PD.xlsx; Syst8_PD.xlsx; Syst9_PD.xlsx | FINAL_PD_INPUTS | Time=0 excluded; no variable-specific alignment correction.
PVsyst A/B/C | PVsyst_3_PD_h.xlsx; PVsyst_8_PD_h.xlsx; PVsyst_9_PD_h.xlsx | FINAL_PD_INPUTS | Internal arbitrary calendar years ignored; row order retained.
Weather-bin geometry | FULL_AZIMUTH_AWARE_PVLIB_AOI + documented Esc=1361.1 Eextn + CIVIL_TIME | UNVERIFIED | Must reproduce frozen weather-bin results before acceptance.

## Master_Long
source_table | System | Software | Sky_condition | period | n | metric_name | metric_value
Annual_GTI | A | IDA ICE |  |  | 4635 | mean_measured | 232.8119
Annual_GTI | A | PVsyst |  |  | 4635 | mean_measured | 232.8119
Annual_GTI | B | IDA ICE |  |  | 5351 | mean_measured | 197.4834
Annual_GTI | B | PVsyst |  |  | 5351 | mean_measured | 197.4834
Annual_GTI | C | IDA ICE |  |  | 5351 | mean_measured | 197.4834
Annual_GTI | C | PVsyst |  |  | 5351 | mean_measured | 197.4834
Annual_GTI | A | IDA ICE |  |  | 4635 | RMSE | 15.3363
Annual_GTI | A | PVsyst |  |  | 4635 | RMSE | 22.4383
Annual_GTI | B | IDA ICE |  |  | 5351 | RMSE | 21.7376
Annual_GTI | B | PVsyst |  |  | 5351 | RMSE | 25.0612
Annual_GTI | C | IDA ICE |  |  | 5351 | RMSE | 21.6221
Annual_GTI | C | PVsyst |  |  | 5351 | RMSE | 26.8748
Annual_GTI | A | IDA ICE |  |  | 4635 | MAE | 10.1623
Annual_GTI | A | PVsyst |  |  | 4635 | MAE | 15.8832
Annual_GTI | B | IDA ICE |  |  | 5351 | MAE | 10.0664
Annual_GTI | B | PVsyst |  |  | 5351 | MAE | 13.8645
Annual_GTI | C | IDA ICE |  |  | 5351 | MAE | 9.9493
Annual_GTI | C | PVsyst |  |  | 5351 | MAE | 15.6754
Annual_GTI | A | IDA ICE |  |  | 4635 | CVRMSE_percent | 6.5874
Annual_GTI | A | PVsyst |  |  | 4635 | CVRMSE_percent | 9.638
Annual_GTI | B | IDA ICE |  |  | 5351 | CVRMSE_percent | 11.0073
Annual_GTI | B | PVsyst |  |  | 5351 | CVRMSE_percent | 12.6903
Annual_GTI | C | IDA ICE |  |  | 5351 | CVRMSE_percent | 10.9488
Annual_GTI | C | PVsyst |  |  | 5351 | CVRMSE_percent | 13.6086
Annual_GTI | A | IDA ICE |  |  | 4635 | nMAE_percent | 4.365
Annual_GTI | A | PVsyst |  |  | 4635 | nMAE_percent | 6.8223
Annual_GTI | B | IDA ICE |  |  | 5351 | nMAE_percent | 5.0973
Annual_GTI | B | PVsyst |  |  | 5351 | nMAE_percent | 7.0206
Annual_GTI | C | IDA ICE |  |  | 5351 | nMAE_percent | 5.038
Annual_GTI | C | PVsyst |  |  | 5351 | nMAE_percent | 7.9376
Annual_GTI | A | IDA ICE |  |  | 4635 | MBE | -9.334
Annual_GTI | A | PVsyst |  |  | 4635 | MBE | -15.75
Annual_GTI | B | IDA ICE |  |  | 5351 | MBE | -7.4245
Annual_GTI | B | PVsyst |  |  | 5351 | MBE | -12.3311
Annual_GTI | C | IDA ICE |  |  | 5351 | MBE | -7.2229
Annual_GTI | C | PVsyst |  |  | 5351 | MBE | -14.1774
Annual_GTI | A | IDA ICE |  |  | 4635 | nMBE_percent | -4.0092
Annual_GTI | A | PVsyst |  |  | 4635 | nMBE_percent | -6.7651
Annual_GTI | B | IDA ICE |  |  | 5351 | nMBE_percent | -3.7595
Annual_GTI | B | PVsyst |  |  | 5351 | nMBE_percent | -6.2441
Annual_GTI | C | IDA ICE |  |  | 5351 | nMBE_percent | -3.6575
Annual_GTI | C | PVsyst |  |  | 5351 | nMBE_percent | -7.179
Annual_GTI | A | IDA ICE |  |  | 4635 | RE_percent | -4.0092
Annual_GTI | A | PVsyst |  |  | 4635 | RE_percent | -6.7651
Annual_GTI | B | IDA ICE |  |  | 5351 | RE_percent | -3.7595
Annual_GTI | B | PVsyst |  |  | 5351 | RE_percent | -6.2441
Annual_GTI | C | IDA ICE |  |  | 5351 | RE_percent | -3.6575
Annual_GTI | C | PVsyst |  |  | 5351 | RE_percent | -7.179
Annual_GTI | A | IDA ICE |  |  | 4635 | R2 | 0.99674
Annual_GTI | A | PVsyst |  |  | 4635 | R2 | 0.99302
Annual_GTI | B | IDA ICE |  |  | 5351 | R2 | 0.99317
Annual_GTI | B | PVsyst |  |  | 5351 | R2 | 0.99093
Annual_GTI | C | IDA ICE |  |  | 5351 | R2 | 0.99325
Annual_GTI | C | PVsyst |  |  | 5351 | R2 | 0.98957
Annual_Temperature | A | IDA ICE |  |  | 4635 | mean_measured | 15.3679
Annual_Temperature | A | PVsyst |  |  | 4635 | mean_measured | 15.3679
Annual_Temperature | B | IDA ICE |  |  | 5351 | mean_measured | 14.4711
Annual_Temperature | B | PVsyst |  |  | 5351 | mean_measured | 14.4711
Annual_Temperature | C | IDA ICE |  |  | 4828 | mean_measured | 17.5758
Annual_Temperature | C | PVsyst |  |  | 4828 | mean_measured | 17.5758
Annual_Temperature | A | IDA ICE |  |  | 4635 | RMSE | 5.1013
Annual_Temperature | A | PVsyst |  |  | 4635 | RMSE | 5.6627
Annual_Temperature | B | IDA ICE |  |  | 5351 | RMSE | 4.7172
Annual_Temperature | B | PVsyst |  |  | 5351 | RMSE | 6.3993
Annual_Temperature | C | IDA ICE |  |  | 4828 | RMSE | 4.44
Annual_Temperature | C | PVsyst |  |  | 4828 | RMSE | 5.5856
Annual_Temperature | A | IDA ICE |  |  | 4635 | MAE | 3.566
Annual_Temperature | A | PVsyst |  |  | 4635 | MAE | 4.1475
Annual_Temperature | B | IDA ICE |  |  | 5351 | MAE | 3.3059
Annual_Temperature | B | PVsyst |  |  | 5351 | MAE | 4.4376
Annual_Temperature | C | IDA ICE |  |  | 4828 | MAE | 3.0585
Annual_Temperature | C | PVsyst |  |  | 4828 | MAE | 3.8606
Annual_Temperature | A | IDA ICE |  |  | 4635 | CVRMSE_percent | 33.1947
Annual_Temperature | A | PVsyst |  |  | 4635 | CVRMSE_percent | 36.8475
Annual_Temperature | B | IDA ICE |  |  | 5351 | CVRMSE_percent | 32.5974
Annual_Temperature | B | PVsyst |  |  | 5351 | CVRMSE_percent | 44.2209
Annual_Temperature | C | IDA ICE |  |  | 4828 | CVRMSE_percent | 25.2623
Annual_Temperature | C | PVsyst |  |  | 4828 | CVRMSE_percent | 31.7803
Annual_Temperature | A | IDA ICE |  |  | 4635 | nMAE_percent | 23.204
Annual_Temperature | A | PVsyst |  |  | 4635 | nMAE_percent | 26.9879
Annual_Temperature | B | IDA ICE |  |  | 5351 | nMAE_percent | 22.845
Annual_Temperature | B | PVsyst |  |  | 5351 | nMAE_percent | 30.6651
Annual_Temperature | C | IDA ICE |  |  | 4828 | nMAE_percent | 17.4017
Annual_Temperature | C | PVsyst |  |  | 4828 | nMAE_percent | 21.9655
Annual_Temperature | A | IDA ICE |  |  | 4635 | MBE | 2.5802
Annual_Temperature | A | PVsyst |  |  | 4635 | MBE | 2.2986
Annual_Temperature | B | IDA ICE |  |  | 5351 | MBE | 1.1289
Annual_Temperature | B | PVsyst |  |  | 5351 | MBE | 0.72761
Annual_Temperature | C | IDA ICE |  |  | 4828 | MBE | -1.4256
Annual_Temperature | C | PVsyst |  |  | 4828 | MBE | -0.3151
Annual_Temperature | A | IDA ICE |  |  | 4635 | nMBE_percent | 16.7897
Annual_Temperature | A | PVsyst |  |  | 4635 | nMBE_percent | 14.9571
Annual_Temperature | B | IDA ICE |  |  | 5351 | nMBE_percent | 7.8011
Annual_Temperature | B | PVsyst |  |  | 5351 | nMBE_percent | 5.028
Annual_Temperature | C | IDA ICE |  |  | 4828 | nMBE_percent | -8.1112
Annual_Temperature | C | PVsyst |  |  | 4828 | nMBE_percent | -1.7928
Annual_Temperature | A | IDA ICE |  |  | 4635 | RE_percent | 16.7897
Annual_Temperature | A | PVsyst |  |  | 4635 | RE_percent | 14.9571
Annual_Temperature | B | IDA ICE |  |  | 5351 | RE_percent | 7.8011
Annual_Temperature | B | PVsyst |  |  | 5351 | RE_percent | 5.028
Annual_Temperature | C | IDA ICE |  |  | 4828 | RE_percent | -8.1112
Annual_Temperature | C | PVsyst |  |  | 4828 | RE_percent | -1.7928
Annual_Temperature | A | IDA ICE |  |  | 4635 | R2 | 0.83562
Annual_Temperature | A | PVsyst |  |  | 4635 | R2 | 0.79745
Annual_Temperature | B | IDA ICE |  |  | 5351 | R2 | 0.84745
Annual_Temperature | B | PVsyst |  |  | 5351 | R2 | 0.71926
Annual_Temperature | C | IDA ICE |  |  | 4828 | R2 | 0.93184
Annual_Temperature | C | PVsyst |  |  | 4828 | R2 | 0.89214
Annual_Power | A | IDA ICE |  |  | 4631 | Common_power_timestamps_removed | 4
Annual_Power | A | PVsyst |  |  | 4631 | Common_power_timestamps_removed | 4
Annual_Power | B | IDA ICE |  |  | 5347 | Common_power_timestamps_removed | 4
Annual_Power | B | PVsyst |  |  | 5347 | Common_power_timestamps_removed | 4
Annual_Power | C | IDA ICE |  |  | 5347 | Common_power_timestamps_removed | 4
Annual_Power | C | PVsyst |  |  | 5347 | Common_power_timestamps_removed | 4
Annual_Power | A | IDA ICE |  |  | 4631 | RMSE_month_kWh_per_kWp | 2.9178
Annual_Power | A | PVsyst |  |  | 4631 | RMSE_month_kWh_per_kWp | 4.1685
Annual_Power | B | IDA ICE |  |  | 5347 | RMSE_month_kWh_per_kWp | 5.7028
Annual_Power | B | PVsyst |  |  | 5347 | RMSE_month_kWh_per_kWp | 2.7157
Annual_Power | C | IDA ICE |  |  | 5347 | RMSE_month_kWh_per_kWp | 9.199
Annual_Power | C | PVsyst |  |  | 5347 | RMSE_month_kWh_per_kWp | 11.3616
Annual_Power | A | IDA ICE |  |  | 4631 | mean_measured | 761.2563
Annual_Power | A | PVsyst |  |  | 4631 | mean_measured | 761.2563
Annual_Power | B | IDA ICE |  |  | 5347 | mean_measured | 770.04
Annual_Power | B | PVsyst |  |  | 5347 | mean_measured | 770.04
Annual_Power | C | IDA ICE |  |  | 5347 | mean_measured | 509.6367
Annual_Power | C | PVsyst |  |  | 5347 | mean_measured | 509.6367
Annual_Power | A | IDA ICE |  |  | 4631 | RMSE | 262.1458
Annual_Power | A | PVsyst |  |  | 4631 | RMSE | 257.2306
Annual_Power | B | IDA ICE |  |  | 5347 | RMSE | 320.5248
Annual_Power | B | PVsyst |  |  | 5347 | RMSE | 294.335
Annual_Power | C | IDA ICE |  |  | 5347 | RMSE | 245.0861
Annual_Power | C | PVsyst |  |  | 5347 | RMSE | 230.4953
Annual_Power | A | IDA ICE |  |  | 4631 | MAE | 167.3538
Annual_Power | A | PVsyst |  |  | 4631 | MAE | 164.9329
Annual_Power | B | IDA ICE |  |  | 5347 | MAE | 179.227
Annual_Power | B | PVsyst |  |  | 5347 | MAE | 161.7188
Annual_Power | C | IDA ICE |  |  | 5347 | MAE | 135.3857
Annual_Power | C | PVsyst |  |  | 5347 | MAE | 127.0654
Annual_Power | A | IDA ICE |  |  | 4631 | CVRMSE_percent | 34.4359
Annual_Power | A | PVsyst |  |  | 4631 | CVRMSE_percent | 33.7903
Annual_Power | B | IDA ICE |  |  | 5347 | CVRMSE_percent | 41.6244
Annual_Power | B | PVsyst |  |  | 5347 | CVRMSE_percent | 38.2233
Annual_Power | C | IDA ICE |  |  | 5347 | CVRMSE_percent | 48.0903
Annual_Power | C | PVsyst |  |  | 5347 | CVRMSE_percent | 45.2274
Annual_Power | A | IDA ICE |  |  | 4631 | nMAE_percent | 21.9839
Annual_Power | A | PVsyst |  |  | 4631 | nMAE_percent | 21.6659
Annual_Power | B | IDA ICE |  |  | 5347 | nMAE_percent | 23.275
Annual_Power | B | PVsyst |  |  | 5347 | nMAE_percent | 21.0014
Annual_Power | C | IDA ICE |  |  | 5347 | nMAE_percent | 26.5651
Annual_Power | C | PVsyst |  |  | 5347 | nMAE_percent | 24.9325
Annual_Power | A | IDA ICE |  |  | 4631 | MBE | 14.0566
Annual_Power | A | PVsyst |  |  | 4631 | MBE | -24.7124
Annual_Power | B | IDA ICE |  |  | 5347 | MBE | 48.0584
Annual_Power | B | PVsyst |  |  | 5347 | MBE | 16.7882
Annual_Power | C | IDA ICE |  |  | 5347 | MBE | 50.3466
Annual_Power | C | PVsyst |  |  | 5347 | MBE | 68.2501
Annual_Power | A | IDA ICE |  |  | 4631 | nMBE_percent | 1.8465
Annual_Power | A | PVsyst |  |  | 4631 | nMBE_percent | -3.2463
Annual_Power | B | IDA ICE |  |  | 5347 | nMBE_percent | 6.241
Annual_Power | B | PVsyst |  |  | 5347 | nMBE_percent | 2.1802
Annual_Power | C | IDA ICE |  |  | 5347 | nMBE_percent | 9.8789
Annual_Power | C | PVsyst |  |  | 5347 | nMBE_percent | 13.3919
Annual_Power | A | IDA ICE |  |  | 4631 | RE_percent | 1.8465
Annual_Power | A | PVsyst |  |  | 4631 | RE_percent | -3.2463
Annual_Power | B | IDA ICE |  |  | 5347 | RE_percent | 6.241
Annual_Power | B | PVsyst |  |  | 5347 | RE_percent | 2.1802
Annual_Power | C | IDA ICE |  |  | 5347 | RE_percent | 9.8789
Annual_Power | C | PVsyst |  |  | 5347 | RE_percent | 13.3919
Annual_Power | A | IDA ICE |  |  | 4631 | R2 | 0.91754
Annual_Power | A | PVsyst |  |  | 4631 | R2 | 0.9206
Annual_Power | B | IDA ICE |  |  | 5347 | R2 | 0.91108
Annual_Power | B | PVsyst |  |  | 5347 | R2 | 0.92502
Annual_Power | C | IDA ICE |  |  | 5347 | R2 | 0.89105
Annual_Power | C | PVsyst |  |  | 5347 | R2 | 0.90363
Monthly_RMSE | A | IDA ICE |  |  |  | kWp | 3.9
Monthly_RMSE | A | PVsyst |  |  |  | kWp | 3.9
Monthly_RMSE | B | IDA ICE |  |  |  | kWp | 4.8
Monthly_RMSE | B | PVsyst |  |  |  | kWp | 4.8
Monthly_RMSE | C | IDA ICE |  |  |  | kWp | 3.3
Monthly_RMSE | C | PVsyst |  |  |  | kWp | 3.3
Monthly_RMSE | A | IDA ICE |  |  |  | n_months | 12
Monthly_RMSE | A | PVsyst |  |  |  | n_months | 12
Monthly_RMSE | B | IDA ICE |  |  |  | n_months | 12
Monthly_RMSE | B | PVsyst |  |  |  | n_months | 12
Monthly_RMSE | C | IDA ICE |  |  |  | n_months | 12
Monthly_RMSE | C | PVsyst |  |  |  | n_months | 12
Monthly_RMSE | A | IDA ICE |  |  |  | RMSE_month_kWh | 11.3795
Monthly_RMSE | A | PVsyst |  |  |  | RMSE_month_kWh | 16.257
Monthly_RMSE | B | IDA ICE |  |  |  | RMSE_month_kWh | 27.3733
Monthly_RMSE | B | PVsyst |  |  |  | RMSE_month_kWh | 13.0354
Monthly_RMSE | C | IDA ICE |  |  |  | RMSE_month_kWh | 30.3568
Monthly_RMSE | C | PVsyst |  |  |  | RMSE_month_kWh | 37.4932
Monthly_RMSE | A | IDA ICE |  |  |  | RMSE_month_kWh_per_kWp | 2.9178
Monthly_RMSE | A | PVsyst |  |  |  | RMSE_month_kWh_per_kWp | 4.1685
Monthly_RMSE | B | IDA ICE |  |  |  | RMSE_month_kWh_per_kWp | 5.7028
Monthly_RMSE | B | PVsyst |  |  |  | RMSE_month_kWh_per_kWp | 2.7157
Monthly_RMSE | C | IDA ICE |  |  |  | RMSE_month_kWh_per_kWp | 9.199
Monthly_RMSE | C | PVsyst |  |  |  | RMSE_month_kWh_per_kWp | 11.3616
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | kt_min | 0
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | kt_min | 0
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | kt_min | 0.2
Weather_Bins | A | PVsyst | Cloudy |  | 651 | kt_min | 0.2
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | kt_min | 0.4
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | kt_min | 0.4
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | kt_min | 0.6
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | kt_min | 0.6
Weather_Bins | A | IDA ICE | Clear |  | 337 | kt_min | 0.75
Weather_Bins | A | PVsyst | Clear |  | 337 | kt_min | 0.75
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | kt_min | 0
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | kt_min | 0
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | kt_min | 0.2
Weather_Bins | B | PVsyst | Cloudy |  | 611 | kt_min | 0.2
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | kt_min | 0.4
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | kt_min | 0.4
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | kt_min | 0.6
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | kt_min | 0.6
Weather_Bins | B | IDA ICE | Clear |  | 350 | kt_min | 0.75
Weather_Bins | B | PVsyst | Clear |  | 350 | kt_min | 0.75
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | kt_min | 0
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | kt_min | 0
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | kt_min | 0.2
Weather_Bins | C | PVsyst | Cloudy |  | 611 | kt_min | 0.2
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | kt_min | 0.4
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | kt_min | 0.4
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | kt_min | 0.6
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | kt_min | 0.6
Weather_Bins | C | IDA ICE | Clear |  | 350 | kt_min | 0.75
Weather_Bins | C | PVsyst | Clear |  | 350 | kt_min | 0.75
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | kt_max | 0.2
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | kt_max | 0.2
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | kt_max | 0.4
Weather_Bins | A | PVsyst | Cloudy |  | 651 | kt_max | 0.4
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | kt_max | 0.6
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | kt_max | 0.6
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | kt_max | 0.75
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | kt_max | 0.75
Weather_Bins | A | IDA ICE | Clear |  | 337 | kt_max
Weather_Bins | A | PVsyst | Clear |  | 337 | kt_max
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | kt_max | 0.2
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | kt_max | 0.2
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | kt_max | 0.4
Weather_Bins | B | PVsyst | Cloudy |  | 611 | kt_max | 0.4
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | kt_max | 0.6
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | kt_max | 0.6
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | kt_max | 0.75
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | kt_max | 0.75
Weather_Bins | B | IDA ICE | Clear |  | 350 | kt_max
Weather_Bins | B | PVsyst | Clear |  | 350 | kt_max
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | kt_max | 0.2
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | kt_max | 0.2
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | kt_max | 0.4
Weather_Bins | C | PVsyst | Cloudy |  | 611 | kt_max | 0.4
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | kt_max | 0.6
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | kt_max | 0.6
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | kt_max | 0.75
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | kt_max | 0.75
Weather_Bins | C | IDA ICE | Clear |  | 350 | kt_max
Weather_Bins | C | PVsyst | Clear |  | 350 | kt_max
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | mean_measured | 211.8795
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | mean_measured | 211.8795
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | mean_measured | 845.318
Weather_Bins | A | PVsyst | Cloudy |  | 651 | mean_measured | 845.318
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | mean_measured | 1617.1499
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | mean_measured | 1617.1499
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | mean_measured | 2475.9879
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | mean_measured | 2475.9879
Weather_Bins | A | IDA ICE | Clear |  | 337 | mean_measured | 2303.1401
Weather_Bins | A | PVsyst | Clear |  | 337 | mean_measured | 2303.1401
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | mean_measured | 242.4531
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | mean_measured | 242.4531
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | mean_measured | 1032.2701
Weather_Bins | B | PVsyst | Cloudy |  | 611 | mean_measured | 1032.2701
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | mean_measured | 1966.3175
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | mean_measured | 1966.3175
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | mean_measured | 3005.0825
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | mean_measured | 3005.0825
Weather_Bins | B | IDA ICE | Clear |  | 350 | mean_measured | 2764.4097
Weather_Bins | B | PVsyst | Clear |  | 350 | mean_measured | 2764.4097
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | mean_measured | 138.9228
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | mean_measured | 138.9228
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | mean_measured | 686.6083
Weather_Bins | C | PVsyst | Cloudy |  | 611 | mean_measured | 686.6083
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | mean_measured | 1344.4597
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | mean_measured | 1344.4597
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | mean_measured | 2052.9757
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | mean_measured | 2052.9757
Weather_Bins | C | IDA ICE | Clear |  | 350 | mean_measured | 1886.4931
Weather_Bins | C | PVsyst | Clear |  | 350 | mean_measured | 1886.4931
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | RMSE | 142.6249
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | RMSE | 137.6264
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | RMSE | 325.8532
Weather_Bins | A | PVsyst | Cloudy |  | 651 | RMSE | 310.0629
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | RMSE | 445.137
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | RMSE | 409.4331
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | RMSE | 394.2061
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | RMSE | 375.1295
Weather_Bins | A | IDA ICE | Clear |  | 337 | RMSE | 350.7667
Weather_Bins | A | PVsyst | Clear |  | 337 | RMSE | 401.0179
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | RMSE | 181.0286
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | RMSE | 172.8227
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | RMSE | 454.3769
Weather_Bins | B | PVsyst | Cloudy |  | 611 | RMSE | 419.2508
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | RMSE | 581.498
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | RMSE | 525.7504
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | RMSE | 484.0586
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | RMSE | 429.9252
Weather_Bins | B | IDA ICE | Clear |  | 350 | RMSE | 557.4638
Weather_Bins | B | PVsyst | Clear |  | 350 | RMSE | 528.6875
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | RMSE | 125.5317
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | RMSE | 130.3364
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | RMSE | 326.5785
Weather_Bins | C | PVsyst | Cloudy |  | 611 | RMSE | 343.8738
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | RMSE | 436.653
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | RMSE | 431.1267
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | RMSE | 449.5008
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | RMSE | 364.0345
Weather_Bins | C | IDA ICE | Clear |  | 350 | RMSE | 430.1902
Weather_Bins | C | PVsyst | Clear |  | 350 | RMSE | 369.5228
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | MAE | 78.7722
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | MAE | 72.8604
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | MAE | 255.6013
Weather_Bins | A | PVsyst | Cloudy |  | 651 | MAE | 239.7571
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | MAE | 367.9939
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | MAE | 332.8335
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | MAE | 297.3623
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | MAE | 296.9788
Weather_Bins | A | IDA ICE | Clear |  | 337 | MAE | 287.9792
Weather_Bins | A | PVsyst | Clear |  | 337 | MAE | 359.8103
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | MAE | 100.8154
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | MAE | 92.8363
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | MAE | 369.4714
Weather_Bins | B | PVsyst | Cloudy |  | 611 | MAE | 329.8869
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | MAE | 470.0925
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | MAE | 406.4038
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | MAE | 364.7746
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | MAE | 322.5754
Weather_Bins | B | IDA ICE | Clear |  | 350 | MAE | 345.2145
Weather_Bins | B | PVsyst | Clear |  | 350 | MAE | 369.7816
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | MAE | 64.7519
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | MAE | 75.8537
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | MAE | 265.4537
Weather_Bins | C | PVsyst | Cloudy |  | 611 | MAE | 283.563
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | MAE | 362.7521
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | MAE | 356.685
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | MAE | 382.4513
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | MAE | 285.8458
Weather_Bins | C | IDA ICE | Clear |  | 350 | MAE | 284.4191
Weather_Bins | C | PVsyst | Clear |  | 350 | MAE | 203.5315
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | CVRMSE_percent | 67.3142
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | CVRMSE_percent | 64.955
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | CVRMSE_percent | 38.548
Weather_Bins | A | PVsyst | Cloudy |  | 651 | CVRMSE_percent | 36.68
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | CVRMSE_percent | 27.526
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | CVRMSE_percent | 25.3182
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | CVRMSE_percent | 15.9212
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | CVRMSE_percent | 15.1507
Weather_Bins | A | IDA ICE | Clear |  | 337 | CVRMSE_percent | 15.2299
Weather_Bins | A | PVsyst | Clear |  | 337 | CVRMSE_percent | 17.4118
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | CVRMSE_percent | 74.6654
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | CVRMSE_percent | 71.2809
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | CVRMSE_percent | 44.0172
Weather_Bins | B | PVsyst | Cloudy |  | 611 | CVRMSE_percent | 40.6144
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | CVRMSE_percent | 29.5729
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | CVRMSE_percent | 26.7378
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | CVRMSE_percent | 16.108
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | CVRMSE_percent | 14.3066
Weather_Bins | B | IDA ICE | Clear |  | 350 | CVRMSE_percent | 20.1657
Weather_Bins | B | PVsyst | Clear |  | 350 | CVRMSE_percent | 19.1248
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | CVRMSE_percent | 90.3608
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | CVRMSE_percent | 93.8193
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | CVRMSE_percent | 47.564
Weather_Bins | C | PVsyst | Cloudy |  | 611 | CVRMSE_percent | 50.083
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | CVRMSE_percent | 32.478
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | CVRMSE_percent | 32.0669
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | CVRMSE_percent | 21.8951
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | CVRMSE_percent | 17.732
Weather_Bins | C | IDA ICE | Clear |  | 350 | CVRMSE_percent | 22.8037
Weather_Bins | C | PVsyst | Clear |  | 350 | CVRMSE_percent | 19.5878
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | nMAE_percent | 37.1778
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | nMAE_percent | 34.3877
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | nMAE_percent | 30.2373
Weather_Bins | A | PVsyst | Cloudy |  | 651 | nMAE_percent | 28.363
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | nMAE_percent | 22.7557
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | nMAE_percent | 20.5815
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | nMAE_percent | 12.0098
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | nMAE_percent | 11.9944
Weather_Bins | A | IDA ICE | Clear |  | 337 | nMAE_percent | 12.5038
Weather_Bins | A | PVsyst | Clear |  | 337 | nMAE_percent | 15.6226
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | nMAE_percent | 41.5814
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | nMAE_percent | 38.2904
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | nMAE_percent | 35.7921
Weather_Bins | B | PVsyst | Cloudy |  | 611 | nMAE_percent | 31.9574
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | nMAE_percent | 23.9073
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | nMAE_percent | 20.6683
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | nMAE_percent | 12.1386
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | nMAE_percent | 10.7343
Weather_Bins | B | IDA ICE | Clear |  | 350 | nMAE_percent | 12.4878
Weather_Bins | B | PVsyst | Clear |  | 350 | nMAE_percent | 13.3765
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | nMAE_percent | 46.61
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | nMAE_percent | 54.6013
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | nMAE_percent | 38.6616
Weather_Bins | C | PVsyst | Cloudy |  | 611 | nMAE_percent | 41.2991
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | nMAE_percent | 26.9813
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | nMAE_percent | 26.53
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | nMAE_percent | 18.6291
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | nMAE_percent | 13.9235
Weather_Bins | C | IDA ICE | Clear |  | 350 | nMAE_percent | 15.0766
Weather_Bins | C | PVsyst | Clear |  | 350 | nMAE_percent | 10.7889
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | MBE | -8.7137
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | MBE | -12.8829
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | MBE | 107.4854
Weather_Bins | A | PVsyst | Cloudy |  | 651 | MBE | 63.2554
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | MBE | 189.3153
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | MBE | 101.7948
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | MBE | 122.515
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | MBE | -37.2814
Weather_Bins | A | IDA ICE | Clear |  | 337 | MBE | -109.1914
Weather_Bins | A | PVsyst | Clear |  | 337 | MBE | -251.1395
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | MBE | -2.9692
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | MBE | 3.7651
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | MBE | 186.9837
Weather_Bins | B | PVsyst | Cloudy |  | 611 | MBE | 114.9225
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | MBE | 284.8902
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | MBE | 156.372
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | MBE | 225.5907
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | MBE | 42.3278
Weather_Bins | B | IDA ICE | Clear |  | 350 | MBE | 74.3031
Weather_Bins | B | PVsyst | Clear |  | 350 | MBE | -54.9623
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | MBE | -12.3418
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | MBE | 30.9433
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | MBE | 123.8443
Weather_Bins | C | PVsyst | Cloudy |  | 611 | MBE | 173.1524
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | MBE | 240.4918
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | MBE | 245.2585
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | MBE | 311.5398
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | MBE | 212.4638
Weather_Bins | C | IDA ICE | Clear |  | 350 | MBE | 166.6386
Weather_Bins | C | PVsyst | Clear |  | 350 | MBE | 124.7169
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | nMBE_percent | -4.1126
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | nMBE_percent | -6.0803
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | nMBE_percent | 12.7154
Weather_Bins | A | PVsyst | Cloudy |  | 651 | nMBE_percent | 7.483
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | nMBE_percent | 11.7067
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | nMBE_percent | 6.2947
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | nMBE_percent | 4.9481
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | nMBE_percent | -1.5057
Weather_Bins | A | IDA ICE | Clear |  | 337 | nMBE_percent | -4.741
Weather_Bins | A | PVsyst | Clear |  | 337 | nMBE_percent | -10.9042
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | nMBE_percent | -1.2247
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | nMBE_percent | 1.5529
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | nMBE_percent | 18.1138
Weather_Bins | B | PVsyst | Cloudy |  | 611 | nMBE_percent | 11.133
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | nMBE_percent | 14.4885
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | nMBE_percent | 7.9525
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | nMBE_percent | 7.507
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | nMBE_percent | 1.4085
Weather_Bins | B | IDA ICE | Clear |  | 350 | nMBE_percent | 2.6878
Weather_Bins | B | PVsyst | Clear |  | 350 | nMBE_percent | -1.9882
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | nMBE_percent | -8.884
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | nMBE_percent | 22.2737
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | nMBE_percent | 18.0371
Weather_Bins | C | PVsyst | Cloudy |  | 611 | nMBE_percent | 25.2185
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | nMBE_percent | 17.8876
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | nMBE_percent | 18.2422
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | nMBE_percent | 15.175
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | nMBE_percent | 10.3491
Weather_Bins | C | IDA ICE | Clear |  | 350 | nMBE_percent | 8.8332
Weather_Bins | C | PVsyst | Clear |  | 350 | nMBE_percent | 6.611
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | RE_percent | -4.1126
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | RE_percent | -6.0803
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | RE_percent | 12.7154
Weather_Bins | A | PVsyst | Cloudy |  | 651 | RE_percent | 7.483
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | RE_percent | 11.7067
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | RE_percent | 6.2947
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | RE_percent | 4.9481
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | RE_percent | -1.5057
Weather_Bins | A | IDA ICE | Clear |  | 337 | RE_percent | -4.741
Weather_Bins | A | PVsyst | Clear |  | 337 | RE_percent | -10.9042
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | RE_percent | -1.2247
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | RE_percent | 1.5529
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | RE_percent | 18.1138
Weather_Bins | B | PVsyst | Cloudy |  | 611 | RE_percent | 11.133
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | RE_percent | 14.4885
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | RE_percent | 7.9525
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | RE_percent | 7.507
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | RE_percent | 1.4085
Weather_Bins | B | IDA ICE | Clear |  | 350 | RE_percent | 2.6878
Weather_Bins | B | PVsyst | Clear |  | 350 | RE_percent | -1.9882
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | RE_percent | -8.884
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | RE_percent | 22.2737
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | RE_percent | 18.0371
Weather_Bins | C | PVsyst | Cloudy |  | 611 | RE_percent | 25.2185
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | RE_percent | 17.8876
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | RE_percent | 18.2422
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | RE_percent | 15.175
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | RE_percent | 10.3491
Weather_Bins | C | IDA ICE | Clear |  | 350 | RE_percent | 8.8332
Weather_Bins | C | PVsyst | Clear |  | 350 | RE_percent | 6.611
Weather_Bins | A | IDA ICE | Overcast/very cloudy |  | 1713 | R2 | 0.70121
Weather_Bins | A | PVsyst | Overcast/very cloudy |  | 1713 | R2 | 0.72178
Weather_Bins | A | IDA ICE | Cloudy |  | 651 | R2 | 0.5046
Weather_Bins | A | PVsyst | Cloudy |  | 651 | R2 | 0.55145
Weather_Bins | A | IDA ICE | Mixed/broken |  | 497 | R2 | 0.4002
Weather_Bins | A | PVsyst | Mixed/broken |  | 497 | R2 | 0.49256
Weather_Bins | A | IDA ICE | Mostly clear |  | 336 | R2 | 0.61717
Weather_Bins | A | PVsyst | Mostly clear |  | 336 | R2 | 0.65333
Weather_Bins | A | IDA ICE | Clear |  | 337 | R2 | 0.74072
Weather_Bins | A | PVsyst | Clear |  | 337 | R2 | 0.66111
Weather_Bins | B | IDA ICE | Overcast/very cloudy |  | 1827 | R2 | 0.65645
Weather_Bins | B | PVsyst | Overcast/very cloudy |  | 1827 | R2 | 0.68689
Weather_Bins | B | IDA ICE | Cloudy |  | 611 | R2 | 0.41748
Weather_Bins | B | PVsyst | Cloudy |  | 611 | R2 | 0.50407
Weather_Bins | B | IDA ICE | Mixed/broken |  | 469 | R2 | 0.36732
Weather_Bins | B | PVsyst | Mixed/broken |  | 469 | R2 | 0.48282
Weather_Bins | B | IDA ICE | Mostly clear |  | 311 | R2 | 0.58947
Weather_Bins | B | PVsyst | Mostly clear |  | 311 | R2 | 0.67616
Weather_Bins | B | IDA ICE | Clear |  | 350 | R2 | 0.63295
Weather_Bins | B | PVsyst | Clear |  | 350 | R2 | 0.66987
Weather_Bins | C | IDA ICE | Overcast/very cloudy |  | 1827 | R2 | 0.65516
Weather_Bins | C | PVsyst | Overcast/very cloudy |  | 1827 | R2 | 0.62826
Weather_Bins | C | IDA ICE | Cloudy |  | 611 | R2 | 0.43328
Weather_Bins | C | PVsyst | Cloudy |  | 611 | R2 | 0.37166
Weather_Bins | C | IDA ICE | Mixed/broken |  | 469 | R2 | 0.29632
Weather_Bins | C | PVsyst | Mixed/broken |  | 469 | R2 | 0.31402
Weather_Bins | C | IDA ICE | Mostly clear |  | 311 | R2 | 0.23259
Weather_Bins | C | PVsyst | Mostly clear |  | 311 | R2 | 0.49667
Weather_Bins | C | IDA ICE | Clear |  | 350 | R2 | 0.5147
Weather_Bins | C | PVsyst | Clear |  | 350 | R2 | 0.64192
Shading_Energy | A | IDA ICE |  | Clear_day_2023-06-05 |  | n_intervals | 24
Shading_Energy | A | PVsyst |  | Clear_day_2023-06-05 |  | n_intervals | 24
Shading_Energy | B | IDA ICE |  | Clear_day_2023-06-05 |  | n_intervals | 24
Shading_Energy | B | PVsyst |  | Clear_day_2023-06-05 |  | n_intervals | 24
Shading_Energy | C | IDA ICE |  | Clear_day_2023-06-05 |  | n_intervals | 24
Shading_Energy | C | PVsyst |  | Clear_day_2023-06-05 |  | n_intervals | 24
Shading_Energy | A | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | n_intervals | 24
Shading_Energy | A | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | n_intervals | 24
Shading_Energy | B | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | n_intervals | 24
Shading_Energy | B | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | n_intervals | 24
Shading_Energy | C | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | n_intervals | 24
Shading_Energy | C | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | n_intervals | 24
Shading_Energy | A | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | n_intervals | 1200
Shading_Energy | A | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | n_intervals | 1200
Shading_Energy | B | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | n_intervals | 1200
Shading_Energy | B | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | n_intervals | 1200
Shading_Energy | C | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | n_intervals | 1200
Shading_Energy | C | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | n_intervals | 1200
Shading_Energy | A | IDA ICE |  | Clear_day_2023-06-05 |  | measured_kWh | 24.211
Shading_Energy | A | PVsyst |  | Clear_day_2023-06-05 |  | measured_kWh | 24.211
Shading_Energy | B | IDA ICE |  | Clear_day_2023-06-05 |  | measured_kWh | 30.915
Shading_Energy | B | PVsyst |  | Clear_day_2023-06-05 |  | measured_kWh | 30.915
Shading_Energy | C | IDA ICE |  | Clear_day_2023-06-05 |  | measured_kWh | 20.188
Shading_Energy | C | PVsyst |  | Clear_day_2023-06-05 |  | measured_kWh | 20.188
Shading_Energy | A | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | measured_kWh | 11.281
Shading_Energy | A | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | measured_kWh | 11.281
Shading_Energy | B | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | measured_kWh | 13.867
Shading_Energy | B | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | measured_kWh | 13.867
Shading_Energy | C | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | measured_kWh | 8.856
Shading_Energy | C | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | measured_kWh | 8.856
Shading_Energy | A | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | measured_kWh | 1021.408
Shading_Energy | A | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | measured_kWh | 1021.408
Shading_Energy | B | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | measured_kWh | 1319.352
Shading_Energy | B | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | measured_kWh | 1319.352
Shading_Energy | C | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | measured_kWh | 867.19
Shading_Energy | C | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | measured_kWh | 867.19
Shading_Energy | A | IDA ICE |  | Clear_day_2023-06-05 |  | simulated_kWh | 23.5509
Shading_Energy | A | PVsyst |  | Clear_day_2023-06-05 |  | simulated_kWh | 24.8915
Shading_Energy | B | IDA ICE |  | Clear_day_2023-06-05 |  | simulated_kWh | 28.5841
Shading_Energy | B | PVsyst |  | Clear_day_2023-06-05 |  | simulated_kWh | 30.1111
Shading_Energy | C | IDA ICE |  | Clear_day_2023-06-05 |  | simulated_kWh | 21.2487
Shading_Energy | C | PVsyst |  | Clear_day_2023-06-05 |  | simulated_kWh | 21.7475
Shading_Energy | A | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | simulated_kWh | 11.3287
Shading_Energy | A | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | simulated_kWh | 11.7826
Shading_Energy | B | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | simulated_kWh | 12.6768
Shading_Energy | B | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | simulated_kWh | 14.0736
Shading_Energy | C | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | simulated_kWh | 9.215
Shading_Energy | C | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | simulated_kWh | 9.7397
Shading_Energy | A | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | simulated_kWh | 1019.3436
Shading_Energy | A | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | simulated_kWh | 1020.6063
Shading_Energy | B | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | simulated_kWh | 1220.7186
Shading_Energy | B | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | simulated_kWh | 1294.1203
Shading_Energy | C | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | simulated_kWh | 901.4112
Shading_Energy | C | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | simulated_kWh | 936.6602
Shading_Energy | A | IDA ICE |  | Clear_day_2023-06-05 |  | difference_kWh | -0.66007
Shading_Energy | A | PVsyst |  | Clear_day_2023-06-05 |  | difference_kWh | 0.6805
Shading_Energy | B | IDA ICE |  | Clear_day_2023-06-05 |  | difference_kWh | -2.3309
Shading_Energy | B | PVsyst |  | Clear_day_2023-06-05 |  | difference_kWh | -0.8039
Shading_Energy | C | IDA ICE |  | Clear_day_2023-06-05 |  | difference_kWh | 1.0607
Shading_Energy | C | PVsyst |  | Clear_day_2023-06-05 |  | difference_kWh | 1.5595
Shading_Energy | A | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_kWh | 0.047667
Shading_Energy | A | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_kWh | 0.5016
Shading_Energy | B | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_kWh | -1.1902
Shading_Energy | B | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_kWh | 0.2066
Shading_Energy | C | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_kWh | 0.35903
Shading_Energy | C | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_kWh | 0.8837
Shading_Energy | A | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_kWh | -2.0644
Shading_Energy | A | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_kWh | -0.8017
Shading_Energy | B | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_kWh | -98.6334
Shading_Energy | B | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_kWh | -25.2317
Shading_Energy | C | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_kWh | 34.2212
Shading_Energy | C | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_kWh | 69.4702
Shading_Energy | A | IDA ICE |  | Clear_day_2023-06-05 |  | difference_fraction | -0.027263
Shading_Energy | A | PVsyst |  | Clear_day_2023-06-05 |  | difference_fraction | 0.028107
Shading_Energy | B | IDA ICE |  | Clear_day_2023-06-05 |  | difference_fraction | -0.075396
Shading_Energy | B | PVsyst |  | Clear_day_2023-06-05 |  | difference_fraction | -0.026004
Shading_Energy | C | IDA ICE |  | Clear_day_2023-06-05 |  | difference_fraction | 0.052542
Shading_Energy | C | PVsyst |  | Clear_day_2023-06-05 |  | difference_fraction | 0.077249
Shading_Energy | A | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_fraction | 0.0042254
Shading_Energy | A | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_fraction | 0.044464
Shading_Energy | B | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_fraction | -0.085827
Shading_Energy | B | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_fraction | 0.014899
Shading_Energy | C | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_fraction | 0.040541
Shading_Energy | C | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_fraction | 0.099785
Shading_Energy | A | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_fraction | -0.0020211
Shading_Energy | A | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_fraction | -0.0007849
Shading_Energy | B | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_fraction | -0.074759
Shading_Energy | B | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_fraction | -0.019124
Shading_Energy | C | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_fraction | 0.039462
Shading_Energy | C | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_fraction | 0.08011
Shading_Energy | A | IDA ICE |  | Clear_day_2023-06-05 |  | difference_percent | -2.7263
Shading_Energy | A | PVsyst |  | Clear_day_2023-06-05 |  | difference_percent | 2.8107
Shading_Energy | B | IDA ICE |  | Clear_day_2023-06-05 |  | difference_percent | -7.5396
Shading_Energy | B | PVsyst |  | Clear_day_2023-06-05 |  | difference_percent | -2.6004
Shading_Energy | C | IDA ICE |  | Clear_day_2023-06-05 |  | difference_percent | 5.2542
Shading_Energy | C | PVsyst |  | Clear_day_2023-06-05 |  | difference_percent | 7.7249
Shading_Energy | A | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_percent | 0.42254
Shading_Energy | A | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_percent | 4.4464
Shading_Energy | B | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_percent | -8.5827
Shading_Energy | B | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_percent | 1.4899
Shading_Energy | C | IDA ICE |  | Partly_cloudy_day_2023-05-15 |  | difference_percent | 4.0541
Shading_Energy | C | PVsyst |  | Partly_cloudy_day_2023-05-15 |  | difference_percent | 9.9785
Shading_Energy | A | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_percent | -0.20211
Shading_Energy | A | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_percent | -0.07849
Shading_Energy | B | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_percent | -7.4759
Shading_Energy | B | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_percent | -1.9124
Shading_Energy | C | IDA ICE |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_percent | 3.9462
Shading_Energy | C | PVsyst |  | Full_period_2023-05-01_to_2023-06-19 |  | difference_percent | 8.011
Shading_Hourly | A | IDA ICE |  |  | 932 | mean_measured | 1095.8809
Shading_Hourly | A | PVsyst |  |  | 932 | mean_measured | 1095.8809
Shading_Hourly | B | IDA ICE |  |  | 886 | mean_measured | 1488.9842
Shading_Hourly | B | PVsyst |  |  | 886 | mean_measured | 1488.9842
Shading_Hourly | C | IDA ICE |  |  | 886 | mean_measured | 978.7698
Shading_Hourly | C | PVsyst |  |  | 886 | mean_measured | 978.7698
Shading_Hourly | A | IDA ICE |  |  | 932 | RMSE | 278.1762
Shading_Hourly | A | PVsyst |  |  | 932 | RMSE | 251.7784
Shading_Hourly | B | IDA ICE |  |  | 886 | RMSE | 566.9802
Shading_Hourly | B | PVsyst |  |  | 886 | RMSE | 198.833
Shading_Hourly | C | IDA ICE |  |  | 886 | RMSE | 182.6585
Shading_Hourly | C | PVsyst |  |  | 886 | RMSE | 253.6952
Shading_Hourly | A | IDA ICE |  |  | 932 | MAE | 179.0142
Shading_Hourly | A | PVsyst |  |  | 932 | MAE | 158.8906
Shading_Hourly | B | IDA ICE |  |  | 886 | MAE | 421.6253
Shading_Hourly | B | PVsyst |  |  | 886 | MAE | 114.5949
Shading_Hourly | C | IDA ICE |  |  | 886 | MAE | 104.623
Shading_Hourly | C | PVsyst |  |  | 886 | MAE | 140.0418
Shading_Hourly | A | IDA ICE |  |  | 932 | CVRMSE_percent | 25.3838
Shading_Hourly | A | PVsyst |  |  | 932 | CVRMSE_percent | 22.975
Shading_Hourly | B | IDA ICE |  |  | 886 | CVRMSE_percent | 38.0783
Shading_Hourly | B | PVsyst |  |  | 886 | CVRMSE_percent | 13.3536
Shading_Hourly | C | IDA ICE |  |  | 886 | CVRMSE_percent | 18.6621
Shading_Hourly | C | PVsyst |  |  | 886 | CVRMSE_percent | 25.9198
Shading_Hourly | A | IDA ICE |  |  | 932 | nMAE_percent | 16.3352
Shading_Hourly | A | PVsyst |  |  | 932 | nMAE_percent | 14.4989
Shading_Hourly | B | IDA ICE |  |  | 886 | nMAE_percent | 28.3163
Shading_Hourly | B | PVsyst |  |  | 886 | nMAE_percent | 7.6962
Shading_Hourly | C | IDA ICE |  |  | 886 | nMAE_percent | 10.6892
Shading_Hourly | C | PVsyst |  |  | 886 | nMAE_percent | 14.3079
Shading_Hourly | A | IDA ICE |  |  | 932 | MBE | -2.1646
Shading_Hourly | A | PVsyst |  |  | 932 | MBE | -0.84914
Shading_Hourly | B | IDA ICE |  |  | 886 | MBE | -111.198
Shading_Hourly | B | PVsyst |  |  | 886 | MBE | -28.3699
Shading_Hourly | C | IDA ICE |  |  | 886 | MBE | 38.6244
Shading_Hourly | C | PVsyst |  |  | 886 | MBE | 78.4088
Shading_Hourly | A | IDA ICE |  |  | 932 | nMBE_percent | -0.19752
Shading_Hourly | A | PVsyst |  |  | 932 | nMBE_percent | -0.077485
Shading_Hourly | B | IDA ICE |  |  | 886 | nMBE_percent | -7.468
Shading_Hourly | B | PVsyst |  |  | 886 | nMBE_percent | -1.9053
Shading_Hourly | C | IDA ICE |  |  | 886 | nMBE_percent | 3.9462
Shading_Hourly | C | PVsyst |  |  | 886 | nMBE_percent | 8.011
Shading_Hourly | A | IDA ICE |  |  | 932 | RE_percent | -0.19752
Shading_Hourly | A | PVsyst |  |  | 932 | RE_percent | -0.077485
Shading_Hourly | B | IDA ICE |  |  | 886 | RE_percent | -7.468
Shading_Hourly | B | PVsyst |  |  | 886 | RE_percent | -1.9053
Shading_Hourly | C | IDA ICE |  |  | 886 | RE_percent | 3.9462
Shading_Hourly | C | PVsyst |  |  | 886 | RE_percent | 8.011
Shading_Hourly | A | IDA ICE |  |  | 932 | R2 | 0.93717
Shading_Hourly | A | PVsyst |  |  | 932 | R2 | 0.94852
Shading_Hourly | B | IDA ICE |  |  | 886 | R2 | 0.8437
Shading_Hourly | B | PVsyst |  |  | 886 | R2 | 0.98078
Shading_Hourly | C | IDA ICE |  |  | 886 | R2 | 0.96518
Shading_Hourly | C | PVsyst |  |  | 886 | R2 | 0.93283