## Metrics
Irradiance_method | System | Aggregation | Quantity | Unit | Software | kWp | n | mean_measured | mean_simulated | RMSE | CVRMSE_percent | MAE | nMAE_percent | MBE | nMBE_percent | RE_percent | R2 | RMSE_per_kWp | RMSE_per_kWp_unit
Perez-Driesse | A | Hourly | Power | W | IDA ICE | 3.9 | 4631 | 761.2563 | 775.3129 | 262.1458 | 34.4359 | 167.3538 | 21.9839 | 14.0566 | 1.8465 | 1.8465 | 0.91754 | 67.2169 | W/kWp
Perez-Driesse | A | Hourly | Power | W | PVsyst | 3.9 | 4631 | 761.2563 | 736.5439 | 257.2306 | 33.7903 | 164.9329 | 21.6659 | -24.7124 | -3.2463 | -3.2463 | 0.9206 | 65.9566 | W/kWp
Perez-Driesse | A | Daily | Energy | kWh/day | IDA ICE | 3.9 | 363 | 9.7118 | 9.8911 | 0.80767 | 8.3164 | 0.46264 | 4.7637 | 0.17933 | 1.8465 | 1.8465 | 0.99031 | 0.2071 | kWh/kWp/day
Perez-Driesse | A | Daily | Energy | kWh/day | PVsyst | 3.9 | 363 | 9.7118 | 9.3965 | 0.96927 | 9.9804 | 0.60645 | 6.2445 | -0.31527 | -3.2463 | -3.2463 | 0.98605 | 0.24853 | kWh/kWp/day
Perez-Driesse | A | Monthly | Energy | kWh/month | IDA ICE | 3.9 | 12 | 293.7815 | 299.2062 | 11.3795 | 3.8735 | 7.099 | 2.4164 | 5.4247 | 1.8465 | 1.8465 | 0.99592 | 2.9178 | kWh/kWp/month
Perez-Driesse | A | Monthly | Energy | kWh/month | PVsyst | 3.9 | 12 | 293.7815 | 284.2446 | 16.257 | 5.5337 | 14.3009 | 4.8679 | -9.5369 | -3.2463 | -3.2463 | 0.99167 | 4.1685 | kWh/kWp/month
Perez-Driesse | B | Hourly | Power | W | IDA ICE | 4.8 | 5347 | 770.04 | 818.0984 | 320.5248 | 41.6244 | 179.227 | 23.275 | 48.0584 | 6.241 | 6.241 | 0.91108 | 66.776 | W/kWp
Perez-Driesse | B | Hourly | Power | W | PVsyst | 4.8 | 5347 | 770.04 | 786.8281 | 294.335 | 38.2233 | 161.7188 | 21.0014 | 16.7882 | 2.1802 | 2.1802 | 0.92502 | 61.3198 | W/kWp
Perez-Driesse | B | Daily | Energy | kWh/day | IDA ICE | 4.8 | 364 | 11.3115 | 12.0175 | 1.4235 | 12.5841 | 0.82267 | 7.2729 | 0.70596 | 6.241 | 6.241 | 0.97952 | 0.29655 | kWh/kWp/day
Perez-Driesse | B | Daily | Energy | kWh/day | PVsyst | 4.8 | 364 | 11.3115 | 11.5582 | 1.1647 | 10.2962 | 0.56786 | 5.0202 | 0.24661 | 2.1802 | 2.1802 | 0.98629 | 0.24264 | kWh/kWp/day
Perez-Driesse | B | Monthly | Energy | kWh/month | IDA ICE | 4.8 | 12 | 343.117 | 364.531 | 27.3733 | 7.9778 | 22.0039 | 6.4129 | 21.414 | 6.241 | 6.241 | 0.98423 | 5.7028 | kWh/kWp/month
Perez-Driesse | B | Monthly | Energy | kWh/month | PVsyst | 4.8 | 12 | 343.117 | 350.5975 | 13.0354 | 3.7991 | 8.8783 | 2.5875 | 7.4805 | 2.1802 | 2.1802 | 0.99642 | 2.7157 | kWh/kWp/month
Perez-Driesse | C | Hourly | Power | W | IDA ICE | 3.3 | 5347 | 509.6367 | 559.9833 | 245.0861 | 48.0903 | 135.3857 | 26.5651 | 50.3466 | 9.8789 | 9.8789 | 0.89105 | 74.2685 | W/kWp
Perez-Driesse | C | Hourly | Power | W | PVsyst | 3.3 | 5347 | 509.6367 | 577.8868 | 230.4953 | 45.2274 | 127.0654 | 24.9325 | 68.2501 | 13.3919 | 13.3919 | 0.90363 | 69.8471 | W/kWp
Perez-Driesse | C | Daily | Energy | kWh/day | IDA ICE | 3.3 | 364 | 7.4863 | 8.2259 | 1.3386 | 17.8812 | 0.83713 | 11.1821 | 0.73957 | 9.8789 | 9.8789 | 0.96031 | 0.40565 | kWh/kWp/day
Perez-Driesse | C | Daily | Energy | kWh/day | PVsyst | 3.3 | 364 | 7.4863 | 8.4889 | 1.4289 | 19.0865 | 1.0233 | 13.6686 | 1.0026 | 13.3919 | 13.3919 | 0.95478 | 0.43299 | kWh/kWp/day
Perez-Driesse | C | Monthly | Energy | kWh/month | IDA ICE | 3.3 | 12 | 227.0856 | 249.5192 | 30.3568 | 13.368 | 23.2296 | 10.2294 | 22.4336 | 9.8789 | 9.8789 | 0.95521 | 9.199 | kWh/kWp/month
Perez-Driesse | C | Monthly | Energy | kWh/month | PVsyst | 3.3 | 12 | 227.0856 | 257.4967 | 37.4932 | 16.5106 | 30.5173 | 13.4387 | 30.4111 | 13.3919 | 13.3919 | 0.93167 | 11.3616 | kWh/kWp/month
Engerer2 | A | Hourly | Power | W | IDA ICE | 3.9 | 4631 | 761.2563 | 785.1735 | 283.9506 | 37.3003 | 185.5221 | 24.3705 | 23.9172 | 3.1418 | 3.1418 | 0.90325 | 72.8079 | W/kWp
Engerer2 | A | Hourly | Power | W | PVsyst | 3.9 | 4631 | 761.2563 | 750.9259 | 261.85 | 34.3971 | 166.7208 | 21.9007 | -10.3304 | -1.357 | -1.357 | 0.91773 | 67.141 | W/kWp
Engerer2 | A | Daily | Energy | kWh/day | IDA ICE | 3.9 | 363 | 9.7118 | 10.0169 | 0.9282 | 9.5575 | 0.59355 | 6.1117 | 0.30512 | 3.1418 | 3.1418 | 0.9872 | 0.238 | kWh/kWp/day
Engerer2 | A | Daily | Energy | kWh/day | PVsyst | 3.9 | 363 | 9.7118 | 9.58 | 0.98761 | 10.1692 | 0.64034 | 6.5934 | -0.13179 | -1.357 | -1.357 | 0.98551 | 0.25323 | kWh/kWp/day
Engerer2 | A | Monthly | Energy | kWh/month | IDA ICE | 3.9 | 12 | 293.7815 | 303.0115 | 13.2983 | 4.5266 | 9.3492 | 3.1824 | 9.23 | 3.1418 | 3.1418 | 0.99442 | 3.4098 | kWh/kWp/month
Engerer2 | A | Monthly | Energy | kWh/month | PVsyst | 3.9 | 12 | 293.7815 | 289.7948 | 12.2392 | 4.1661 | 10.4578 | 3.5597 | -3.9867 | -1.357 | -1.357 | 0.99528 | 3.1383 | kWh/kWp/month
Engerer2 | B | Hourly | Power | W | IDA ICE | 4.8 | 5347 | 770.04 | 781.359 | 321.7465 | 41.7831 | 181.9483 | 23.6284 | 11.319 | 1.4699 | 1.4699 | 0.9104 | 67.0305 | W/kWp
Engerer2 | B | Hourly | Power | W | PVsyst | 4.8 | 5347 | 770.04 | 798.0731 | 308.8472 | 40.1079 | 168.186 | 21.8412 | 28.0331 | 3.6405 | 3.6405 | 0.91744 | 64.3432 | W/kWp
Engerer2 | B | Daily | Energy | kWh/day | IDA ICE | 4.8 | 364 | 11.3115 | 11.4778 | 1.3445 | 11.8859 | 0.77802 | 6.8781 | 0.16627 | 1.4699 | 1.4699 | 0.98173 | 0.2801 | kWh/kWp/day
Engerer2 | B | Daily | Energy | kWh/day | PVsyst | 4.8 | 364 | 11.3115 | 11.7233 | 1.3312 | 11.7684 | 0.75425 | 6.668 | 0.41179 | 3.6405 | 3.6405 | 0.98209 | 0.27733 | kWh/kWp/day
Engerer2 | B | Monthly | Energy | kWh/month | IDA ICE | 4.8 | 12 | 343.117 | 348.1606 | 10.7736 | 3.1399 | 8.4764 | 2.4704 | 5.0436 | 1.4699 | 1.4699 | 0.99756 | 2.2445 | kWh/kWp/month
Engerer2 | B | Monthly | Energy | kWh/month | PVsyst | 4.8 | 12 | 343.117 | 355.6081 | 17.2489 | 5.0271 | 12.4911 | 3.6405 | 12.4911 | 3.6405 | 3.6405 | 0.99374 | 3.5935 | kWh/kWp/month
Engerer2 | C | Hourly | Power | W | IDA ICE | 3.3 | 5347 | 509.6367 | 572.1843 | 264.7193 | 51.9427 | 142.7761 | 28.0153 | 62.5476 | 12.273 | 12.273 | 0.87289 | 80.218 | W/kWp
Engerer2 | C | Hourly | Power | W | PVsyst | 3.3 | 5347 | 509.6367 | 586.7755 | 243.8375 | 47.8454 | 133.0241 | 26.1018 | 77.1388 | 15.136 | 15.136 | 0.89215 | 73.8901 | W/kWp
Engerer2 | C | Daily | Energy | kWh/day | IDA ICE | 3.3 | 364 | 7.4863 | 8.4051 | 1.5084 | 20.1487 | 1.0178 | 13.5953 | 0.9188 | 12.273 | 12.273 | 0.94961 | 0.45709 | kWh/kWp/day
Engerer2 | C | Daily | Energy | kWh/day | PVsyst | 3.3 | 364 | 7.4863 | 8.6195 | 1.5932 | 21.2819 | 1.1708 | 15.6388 | 1.1331 | 15.136 | 15.136 | 0.94378 | 0.4828 | kWh/kWp/day
Engerer2 | C | Monthly | Energy | kWh/month | IDA ICE | 3.3 | 12 | 227.0856 | 254.9558 | 35.0852 | 15.4502 | 27.8702 | 12.273 | 27.8702 | 12.273 | 12.273 | 0.94017 | 10.6319 | kWh/kWp/month
Engerer2 | C | Monthly | Energy | kWh/month | PVsyst | 3.3 | 12 | 227.0856 | 261.4574 | 41.6704 | 18.3501 | 34.3718 | 15.136 | 34.3718 | 15.136 | 15.136 | 0.9156 | 12.6274 | kWh/kWp/month

## Paired_comparison
Irradiance_method | System | Aggregation | Quantity | Unit | n_periods | kWp | RMSE_IDA | RMSE_PVsyst | Delta_RMSE_IDA_minus_PVsyst | CVRMSE_IDA_percent | CVRMSE_PVsyst_percent | Delta_CVRMSE_percentage_points | nMBE_IDA_percent | nMBE_PVsyst_percent | Favored_by_RMSE | Favored_by_CVRMSE
Perez-Driesse | A | Hourly | Power | W | 4631 | 3.9 | 262.1458 | 257.2306 | 4.9152 | 34.4359 | 33.7903 | 0.64567 | 1.8465 | -3.2463 | PVsyst | PVsyst
Perez-Driesse | A | Daily | Energy | kWh/day | 363 | 3.9 | 0.80767 | 0.96927 | -0.1616 | 8.3164 | 9.9804 | -1.664 | 1.8465 | -3.2463 | IDA ICE | IDA ICE
Perez-Driesse | A | Monthly | Energy | kWh/month | 12 | 3.9 | 11.3795 | 16.257 | -4.8775 | 3.8735 | 5.5337 | -1.6603 | 1.8465 | -3.2463 | IDA ICE | IDA ICE
Perez-Driesse | B | Hourly | Power | W | 5347 | 4.8 | 320.5248 | 294.335 | 26.1898 | 41.6244 | 38.2233 | 3.4011 | 6.241 | 2.1802 | PVsyst | PVsyst
Perez-Driesse | B | Daily | Energy | kWh/day | 364 | 4.8 | 1.4235 | 1.1647 | 0.25879 | 12.5841 | 10.2962 | 2.2879 | 6.241 | 2.1802 | PVsyst | PVsyst
Perez-Driesse | B | Monthly | Energy | kWh/month | 12 | 4.8 | 27.3733 | 13.0354 | 14.338 | 7.9778 | 3.7991 | 4.1787 | 6.241 | 2.1802 | PVsyst | PVsyst
Perez-Driesse | C | Hourly | Power | W | 5347 | 3.3 | 245.0861 | 230.4953 | 14.5907 | 48.0903 | 45.2274 | 2.863 | 9.8789 | 13.3919 | PVsyst | PVsyst
Perez-Driesse | C | Daily | Energy | kWh/day | 364 | 3.3 | 1.3386 | 1.4289 | -0.090235 | 17.8812 | 19.0865 | -1.2053 | 9.8789 | 13.3919 | IDA ICE | IDA ICE
Perez-Driesse | C | Monthly | Energy | kWh/month | 12 | 3.3 | 30.3568 | 37.4932 | -7.1364 | 13.368 | 16.5106 | -3.1426 | 9.8789 | 13.3919 | IDA ICE | IDA ICE
Engerer2 | A | Hourly | Power | W | 4631 | 3.9 | 283.9506 | 261.85 | 22.1007 | 37.3003 | 34.3971 | 2.9032 | 3.1418 | -1.357 | PVsyst | PVsyst
Engerer2 | A | Daily | Energy | kWh/day | 363 | 3.9 | 0.9282 | 0.98761 | -0.059406 | 9.5575 | 10.1692 | -0.61169 | 3.1418 | -1.357 | IDA ICE | IDA ICE
Engerer2 | A | Monthly | Energy | kWh/month | 12 | 3.9 | 13.2983 | 12.2392 | 1.0591 | 4.5266 | 4.1661 | 0.3605 | 3.1418 | -1.357 | PVsyst | PVsyst
Engerer2 | B | Hourly | Power | W | 5347 | 4.8 | 321.7465 | 308.8472 | 12.8992 | 41.7831 | 40.1079 | 1.6751 | 1.4699 | 3.6405 | PVsyst | PVsyst
Engerer2 | B | Daily | Energy | kWh/day | 364 | 4.8 | 1.3445 | 1.3312 | 0.013295 | 11.8859 | 11.7684 | 0.11754 | 1.4699 | 3.6405 | PVsyst | PVsyst
Engerer2 | B | Monthly | Energy | kWh/month | 12 | 4.8 | 10.7736 | 17.2489 | -6.4754 | 3.1399 | 5.0271 | -1.8872 | 1.4699 | 3.6405 | IDA ICE | IDA ICE
Engerer2 | C | Hourly | Power | W | 5347 | 3.3 | 264.7193 | 243.8375 | 20.8818 | 51.9427 | 47.8454 | 4.0974 | 12.273 | 15.136 | PVsyst | PVsyst
Engerer2 | C | Daily | Energy | kWh/day | 364 | 3.3 | 1.5084 | 1.5932 | -0.084832 | 20.1487 | 21.2819 | -1.1332 | 12.273 | 15.136 | IDA ICE | IDA ICE
Engerer2 | C | Monthly | Energy | kWh/month | 12 | 3.3 | 35.0852 | 41.6704 | -6.5852 | 15.4502 | 18.3501 | -2.8999 | 12.273 | 15.136 | IDA ICE | IDA ICE

## Aggregation_robustness
Irradiance_method | System | Hourly_favored_tool | Daily_favored_tool | Monthly_favored_tool | Favored_tool_same_hourly_daily_monthly | Hourly_Delta_CVRMSE_pp | Daily_Delta_CVRMSE_pp | Monthly_Delta_CVRMSE_pp | Delta_CVRMSE_sign_same_all_scales
Perez-Driesse | A | PVsyst | IDA ICE | IDA ICE | FALSE | 0.64567 | -1.664 | -1.6603 | FALSE
Perez-Driesse | B | PVsyst | PVsyst | PVsyst | TRUE | 3.4011 | 2.2879 | 4.1787 | TRUE
Perez-Driesse | C | PVsyst | IDA ICE | IDA ICE | FALSE | 2.863 | -1.2053 | -3.1426 | FALSE
Engerer2 | A | PVsyst | IDA ICE | PVsyst | FALSE | 2.9032 | -0.61169 | 0.3605 | FALSE
Engerer2 | B | PVsyst | PVsyst | IDA ICE | FALSE | 1.6751 | 0.11754 | -1.8872 | FALSE
Engerer2 | C | PVsyst | IDA ICE | IDA ICE | FALSE | 4.0974 | -1.1332 | -2.8999 | FALSE

## Cross_method
System | Hourly_favored_tool_Engerer2 | Hourly_favored_tool_Perez-Driesse | Daily_favored_tool_Engerer2 | Daily_favored_tool_Perez-Driesse | Monthly_favored_tool_Engerer2 | Monthly_favored_tool_Perez-Driesse | Favored_tool_same_hourly_daily_monthly_Engerer2 | Favored_tool_same_hourly_daily_monthly_Perez-Driesse
A | PVsyst | PVsyst | IDA ICE | IDA ICE | PVsyst | IDA ICE | FALSE | FALSE
B | PVsyst | PVsyst | PVsyst | PVsyst | IDA ICE | PVsyst | FALSE | TRUE
C | PVsyst | PVsyst | IDA ICE | IDA ICE | IDA ICE | IDA ICE | FALSE | FALSE

## Annual_energy
Irradiance_method | System | Software | kWp | Measured_annual_energy_kWh | Simulated_annual_energy_kWh | Annual_energy_difference_kWh | Annual_energy_bias_percent
Perez-Driesse | A | IDA ICE | 3.9 | 3525.3781 | 3590.4742 | 65.0961 | 1.8465
Perez-Driesse | A | PVsyst | 3.9 | 3525.3781 | 3410.935 | -114.4431 | -3.2463
Perez-Driesse | B | IDA ICE | 4.8 | 4117.4038 | 4374.372 | 256.9683 | 6.241
Perez-Driesse | B | PVsyst | 4.8 | 4117.4038 | 4207.1701 | 89.7663 | 2.1802
Perez-Driesse | C | IDA ICE | 3.3 | 2725.0274 | 2994.2305 | 269.2031 | 9.8789
Perez-Driesse | C | PVsyst | 3.3 | 2725.0274 | 3089.9606 | 364.9332 | 13.3919
Engerer2 | A | IDA ICE | 3.9 | 3525.3781 | 3636.1384 | 110.7603 | 3.1418
Engerer2 | A | PVsyst | 3.9 | 3525.3781 | 3477.538 | -47.8401 | -1.357
Engerer2 | B | IDA ICE | 4.8 | 4117.4038 | 4177.9266 | 60.5228 | 1.4699
Engerer2 | B | PVsyst | 4.8 | 4117.4038 | 4267.2969 | 149.8931 | 3.6405
Engerer2 | C | IDA ICE | 3.3 | 2725.0274 | 3059.4694 | 334.442 | 12.273
Engerer2 | C | PVsyst | 3.3 | 2725.0274 | 3137.4886 | 412.4612 | 15.136